## חישוב
להכניס נתון | נתון מחושב
נוסחת החישוב
לפי EINAR GRAN MEYER
| תאור | סימן | יחידות | ערך
| מקדם התפשטות טרמית | ά | למעלת קלווין | 0.00017
| מודול יאנג בזמן אפס | E0 | Mpa | 1100
| טפרטורה 1 | θ 1 | קלוין | 30
| טמפרטורה 2 | θ 2 | קלוין | 20
| הפרש טמפרטורות | Δθ | קלוין | 10
| מאמץ בחומר כתוצאה מהפרש הטמפרטורה | σ | Mpa
נוסחה:
| חישוב: מאמץ בדופן הצינור, כשהצינור רתום, כתוצאה מהפרש הטמפרטורה |  | Mpa ניוטון למילימטר מרובע | 1.87
נתוני צינור
| קוטר חיצוני |  | מילימטר | 160
| SDR |  |  | 17
| עובי דופן |  | מילימטר | 9.4118
| שטח חתך |  | מילימטר מרובע | 4452.5825
| חישוב : כח מתיחה/ דחיפה בצינור, לפי קוטר חיצוני ו SDR |  | ניוטון | 8326.3293
| עומס לפלקס אחד |  | ניוטון | 30000
| מספר פלקס דרושים |  |  | 0.27754
חישוב לפי PPI | פרק 6, עמוד 244 |  |  |  | SECOND EDITION HANDBOOK OF PE PIPE |  | http://plasticpipe.org/publications/pe_handbook.html
| תאור | סימן | יחידות | ערך
| מקדם התפשטות טרמית | ά | in/in/deg F | 0.0001
| מודול יאנג בזמן אפס | E0 | PSI | 159500
| טפרטורה 1 | θ 1 | פרנהייט | 95 | 45 C
| טמפרטורה 2 | θ 2 | פרנהייט | 68 | 30 C
| הפרש טמפרטורות | Δθ | פרנהייט | 27 | 15 C
| מאמץ בחומר כתוצאה מהפרש הטמפרטורה | σ | PSI
|  | σ | PSI | 430.65 | 2.96 MPA
פרק 3, עמוד 99 :
PE pipe -design and installation- M55 , by AWWA , page 4
𝜎=𝐸0∗𝛼∗∆𝜃
𝜎=𝐸0∗𝛼∗∆𝜃

## required qunatity- metric
Plasson - Technical note, May 2021
Required number of restraints calculation
parameter |  | source | value | units | comments
Pipe raw material |  |  | PE100 |  | The calculation is based on theoretical data , for the load induced by the thermal expansion/contraction only. The designer should take in consideration other axial loads if exists.
Elasticity modulus at t=0 (E) |  | manufacturer data | 800 | Mpa
thermal expansion coefficient (K) |  |  | 0.00017 | mm/mm/deg C
temperature change (DT) |  |  | 1 | Celsios
induced tensile stress |  | E*K*DT | 0.136 | n*mm^2
Axial force restrained by one flex restraint |  | Plasson product spec | 32000 | Newton
To calculate the required number of restraints, for rapid temperature change : multiply the temperature change by the axial force (See table below), and divide by 32000 . For graduate temperature change ( t>60 min) : divide by 1.5
Calculation example : for 500 SDR 11 pipe, when the temperature change is 20 C, instant change : N=8828X 20/32000=5.5. 6 restraints required. For graduate temperature change: N=8828X 20/32000 / 1.5 = 3.7 . 4 restraints required
pipe OD, mm | axial force (Newton) induced by rapid temperature change of 1 degree C, acc. to pipe SDR
| 9 | 11 | 17 | 21 | 26 | 32
160 | 1080.2735 | 903.9478 | 605.5512 | 496.0439 | 404.5033 | 331.1239
180 | 1367.2211 | 1144.059 | 766.4008 | 627.8056 | 511.9495 | 419.0786
200 | 1687.9273 | 1412.4185 | 946.1738 | 775.0687 | 632.0364 | 517.381
225 | 2136.283 | 1787.5922 | 1197.5012 | 980.9463 | 799.9211 | 654.8104
250 | 2637.3864 | 2206.9039 | 1478.3965 | 1211.0448 | 987.5569 | 808.4079
280 | 3308.3375 | 2768.3403 | 1854.5006 | 1519.1346 | 1238.7913 | 1014.0668
315 | 4187.1147 | 3503.6807 | 2347.1024 | 1922.6547 | 1567.8453 | 1283.4283
355 | 5318.026 | 4450.0011 | 2981.0388 | 2441.9507 | 1991.3097 | 1630.0736
400 | 6751.7092 | 5649.6741 | 3784.6951 | 3100.2747 | 2528.1456 | 2069.5242
450 | 8545.132 | 7150.3687 | 4790.0048 | 3923.7851 | 3199.6842 | 2619.2415
500 | 10549.5457 | 8827.6157 | 5913.5862 | 4844.1791 | 3950.2274 | 3233.6315
560 | 13233.3501 | 11073.3612 | 7418.0025 | 6076.5383 | 4955.1653 | 4056.2674
630 | 16748.4588 | 14014.7227 | 9388.4094 | 7690.6188 | 6271.3811 | 5133.7134 | Calculation for 1200 SDR 26 pipe : for a gradual temperature change of 30 C between day and night, N = 22753 X 30 / 32000 / 1.5 = 14.22 Therfore, 15 restraints required
710 | 21272.104 | 17800.0043 | 11924.1552 | 9767.8028 | 7965.2386 | 6520.2946
800 | 27006.837 | 22598.6962 | 15138.7806 | 12401.0986 | 10112.5823 | 8278.0966
900 | 34180.5281 | 28601.4749 | 19160.0192 | 15695.1404 | 12798.7369 | 10476.9661
1000 | 42198.1828 | 35310.4629 | 23654.3447 | 19376.7166 | 15800.9098 | 12934.526
1200 | 60765.3832 | 50847.0666 | 34062.2563 | 27902.4719 | 22753.3101 | 18625.7174